## M7 - DSE 7x8x
j1939_threshold
description | resource | sample_payload | device.id | snapshot.pgn_id | snapshot.raw.value | expected_value
Engine Run Status (RPM based) | 0 | 120808befa959a0610321a021004220518990140032a021009320e120c0000e720df639bc7b50100183a11188188c007220a1a08ffffffa10fffffff409702 | 7020016917 | F00401 | FFFFFFA10FFFFFFF | 501 rpm
Modbus Communication Status | 0 | 12090888def9900610e7012001181e5820 | 7020016917
J1939_periodic
Description | resource | device.id | event.registers.value | snapshot.pgn_id | snapshot.raw.value | expecetd.value | status |  | Package Details:
Time to Next Active Regeneration | 2 | 7020016917 |  | FCB901 | 1700A108FFFFFFFF | 1675.56 days | Not Found |  | sources : 0 1 pgn : 64697 spn : 5978 offset : 1 translation : ([value] & 0xffffffffUL) * 0.05h/bit validation : [value] >= 0 && [value] <= 210554061 when : always uom : h flags : none
Time Since Last System Cleaning Event | 2 | 7020016917 |  | FCB901 | FFFFFFFF0A610101 | 195.22 days | Not Found |  | sources : 0 1 pgn : 64697 spn : 6941 offset : 5 translation : (([value] >> 32) & 0xffffffffUL) * 0.05h/bit validation : [value] >= 0 && [value] <= 210554061 when : always uom : h flags : none
Ambient Air Temperature | 2 | 7020016917 |  | FEF501 | FFFFFFC30AFFFFFF | 86.09375 deg C | Not Found |  | sources : 0 1 pgn : 65269 spn : 171 offset : 4-5 translation : ((([value] >> 24) & 0xffffUL) * 0.03125) -273.0 validation : [value] >= -54 && [value] <= 1734 when : always uom : C flags : none
Engine Exhaust Gas Temperature | 2 | 7020016917 |  | FEF601 | FFFFFFFFFF0B10FF | 128.34375 deg C | Not Found |  | sources : 0 1 pgn : 65270 spn : 173 offset : 6-7 translation : ((([value] >> 40) & 0xffffUL) * 0.03125) -273.0 validation : [value] >= -54 && [value] <= 1734 when : always uom : C flags : none
Supply Gas Methane Percentage | 2 | 7020016917 |  | FEFC01 | D01BFFFFFFFFFFFF | 17.8% | Not Found
Gaseous Engine Run Hours | 2 | 7020016917 |  | FCA001 | 0A0100B1FFFFFFFF | 148478374.9 hrs | Not Found |  | sources : 0 1 pgn : 64672 spn : 6319 offset : 1 translation : ([value] & 0xffffffffUL) * 0.05h/bit validation : [value] >= 0 && [value] <= 210554061 when : always uom : h flags : none
Diesel Engine Run Hours | 2 | 7020016917 |  | FCA001 | FFFFFFFF0A010011 | 14260646.9 hrs | Not Found |  | sources : 0 1 pgn : 64672 spn : 6320 offset : 5 translation : (([value] >> 32) & 0xffffffffUL) * 0.05h/bit validation : [value] >= 0 && [value] <= 210554061 when : always uom : h flags : none
Engine Gaseous Fuel Supply Unit Intake Pressure | 2 | 7020016917 |  | FC3A01 | FFFFA720FFFFFFFF | 4179.5 kPa | Not Found |  | sources : 0 1 pgn : 64570 spn : 7064 offset : 1 translation : ([value] & 0xffffUL) * 0.5 kPa/bit validation : [value] >= 0 && [value] <= 32128 when : always uom : kPA flags : none
Engine Total Gaseous Fuel Volume Used | 2 | 7020016917 |  | FC1101 | 0A0100B1FFFFFFFF | 1484783749 m^3 | Not Found |  | sources : 0 1 pgn : 64529 spn : 7455 offset : 1 translation : ([value] & 0xffffffffUL) * 0.5 m^3/bit validation : [value] >= 0 && [value] <= 2105540608 when : always uom : m^3 flags : none
Engine Total Gaseous Idle Fuel Volume Used | 2 | 7020016917 |  | FC1101 | FFFFFFFF0A010011 | 142606469 m^3 | Not Found |  | sources : 0 1 pgn : 64529 spn : 7456 offset : 5 translation : (([value] >> 32) & 0xffffffffUL) * 0.5 m^3/bit validation : [value] >= 0 && [value] <= 2105540608 when : always uom : m^3 flags : none
Fuel Level | 2 | 7020016917 |  | FEFC01 | FF2EFFFFFFFFFFFF | 18.4% | Not Found | FUEL LEVEL PICKED UP VIA MODBUS
Engine Speed | 2 | 7020016917 | 0,0,4199,12767,2974619,0,24 | F00401 | FFFFFFC800FFFFFF | 25 rpm | Pass |  | sources : 0 1 pgn : 61444 spn : 190 offset : 4-5 translation : (([value] >> 24) & 0xffffUL) * 0.125 validation : [value] >= 0 && [value] <= 8031.875 when : always uom : rpm flags : none
Engine Percent Load at Current Speed | 2 | 7020016917 |  | F00301 | FFFF34FFFFFFFFFF | 52% | Pass |  | sources : 0 1 pgn : 61443 spn : 92 offset : 3 translation : ([value] >> 16) & 0xffUL validation : [value] >= 0 && [value] <= 125 when : always uom : % flags : none
Diesel Particulate Filter 1 Soot Load Percent | 2 | 7020016917 |  | FD7B01 | A7FFFFFFFFFFFFFF | 167% | Pass |  | sources : 0 1 pgn : 64891 spn : 3719 offset : 1 translation : [value] & 0xffUL validation : [value] >= 0 && [value] <= 250 when : always uom : % flags : none
Diesel Particulate Filter 1 Ash Load Percent | 2 | 7020016917 |  | FD7B01 | FF0BFFFFFFFFFFFF | 11% | Pass | Offset = - 40 | sources : 0 1 pgn : 64891 spn : 3720 offset : 2 translation : ([value] >> 8) & 0xffUL validation : [value] >= 0 && [value] <= 250 when : always uom : % flags : none
Diesel Particulate Filter 1 Time Since Last Active Regeneration | 2 | 7020016917 |  | FD7B01 | FFFF09B0A100FFFF | 122.64 Days | Pass | Offset = - 273 | sources : 0 1 pgn : 64891 spn : 3721 offset : 3-6 translation : (([value] >> 16) & 0xffffffffUL) * 1.157407407e-05 validation : [value] >= 0 && [value] <= 48739 when : always uom : Days flags : none
DEF / Aftertreatment 1 SCR Catalyst Tank Level | 2 | 7020016917 |  | FE5601 | CBFFFFFFFFFFFFFF | 81.2% | Pass |  | sources : 0 1 pgn : 65110 spn : 1761 offset : 1 translation : ([value] & 0xffUL) * 0.4 validation : [value] >= 0 && [value] <= 100 when : always uom : % flags : none
Engine Total Fuel Used | 2 | 7020016917 |  | FEE901 | FFFFFFFF0A0100A1 | 1350566021 L | Pass |  | sources : 0 1 pgn : 65257 spn : 250 offset : 5-8 translation : (([value] >> 32) & 0xffffffffUL) * 0.5 validation : [value] >= 0 && [value] <= 2105540607.5 when : always uom : l flags : none
Engine Coolant Temperature | 2 | 7020016917 |  | FEEE01 | B1FFFFFFFFFFFFFF | (177-40) = 137 deg C | Pass |  | sources : 0 1 pgn : 65262 spn : 110 offset : 1 translation : ([value] & 0xffUL) -40.0 validation : [value] >= -40 && [value] <= 210 when : always uom : C flags : none
Engine Oil Temperature 1 | 2 | 7020016917 |  | FEEE01 | FFFF01CAFFFFFFFF | (1616.03125 - 237) = 1343.03 deg C | Pass |  | sources : 0 1 pgn : 65262 spn : 175 offset : 3-4 translation : ((([value] >> 16) & 0xffffUL) * 0.03125) -273.0 validation : [value] >= -273 && [value] <= 1734.96875 when : always uom : C flags : none
Engine Oil Pressure | 2 | 7020016917 |  | FEEF01 | FFFFFF1EFFFFFFFF | 120 kPa | Pass |  | sources : 0 1 pgn : 65263 spn : 100 offset : 4 translation : (([value] >> 24) & 0xffUL) * 4.0 validation : [value] >= 0 && [value] <= 1000 when : always uom : kPa flags : none
Engine Fuel Delivery Pressure | 2 | 7020016917 |  | FEEF01 | 4BFFFFFFFFFFFFFF | 300 kPa | Pass |  | sources : 0 1 pgn : 65263 spn : 94 offset : 1 translation : ([value] & 0xffUL) * 4.0 validation : [value] >= 0 && [value] <= 1000 when : always uom : kPa flags : none
Engine Oil Level | 2 | 7020016917 |  | FEEF01 | FFFFD8FFFFFFFFFF | 86.4% | Pass | Offset = - 40 | sources : 0 1 pgn : 65263 spn : 98 offset : 3 translation : (([value] >> 16) & 0xffUL) * 0.4 validation : [value] >= 0 && [value] <= 100 when : always uom : % flags : none
Engine Coolant Level | 2 | 7020016917 |  | FEEF01 | FFFFFFFFFFFFFFE2 | 90.4% | Pass |  | sources : 0 1 pgn : 65263 spn : 111 offset : 8 translation : (([value] >> 56) & 0xffUL) * 0.4 validation : [value] >= 0 && [value] <= 100 when : always uom : % flags : none
Engine Fuel Rate | 2 | 7020016917 |  | FEF201 | A037FFFFFFFFFFFF | 712 L/h | Pass | Offset = - 40 | sources : 0 1 pgn : 65266 spn : 183 offset : 1-2 translation : ([value] & 0xffffUL) * 0.05 validation : [value] >= 0 && [value] <= 3212.75 when : always uom : l/h flags : none
Barometric Pressure | 2 | 7020016917 |  | FEF501 | D1FFFFFFFFFFFFFF | 104.5 kPa | Pass |  | sources : 0 1 pgn : 65269 spn : 108 offset : 1 translation : ([value] & 0xffUL) * 0.5 validation : [value] >= 0 && [value] <= 125 when : always uom : kPa flags : none
Engine Air Inlet Temperature | 2 | 7020016917 |  | FEF501 | FFFFFFFFFF0BFFFF | (11-40) = -29 deg C | Pass |  | sources : 0 1 pgn : 65269 spn : 172 offset : 6 translation : (([value] >> 40) & 0xffUL) -40.0 validation : [value] >= -40 && [value] <= 210 when : always uom : C flags : none
Intake Manifold Pressure | 2 | 7020016917 |  | FEF601 | FF1BFFFFFFFFFFFF | 54 kPa | Pass |  | sources : 0 1 pgn : 65270 spn : 102 offset : 2 translation : (([value] >> 8) & 0xffUL) * 2.0 validation : [value] >= 0 && [value] <= 500 when : always uom : kPa flags : none
Intake Manifold Temperature | 2 | 7020016917 |  | FEF601 | FFFF5EFFFFFFFFFF | (94 - 40) = 54 deg C | Pass |  | sources : 0 1 pgn : 65270 spn : 105 offset : 3 translation : (([value] >> 16) & 0xffUL) -40.0 validation : [value] >= -40 && [value] <= 210 when : always uom : C flags : none
Engine Air Inlet Pressure | 2 | 7020016917 |  | FEF601 | FFFFFF1CFFFFFFFF | 56 kPa | Pass |  | sources : 0 1 pgn : 65270 spn : 106 offset : 4 translation : (([value] >> 24) & 0xffUL) * 2.0 validation : [value] >= 0 && [value] <= 500 when : always uom : kPa flags : none
Engine Air Filter Differential Pressure | 2 | 7020016917 |  | FEF601 | FFFFFFFF5EFFFFFF | 4.7 kPa | Pass |  | sources : 0 1 pgn : 65270 spn : 107 offset : 5 translation : (([value] >> 32) & 0xffUL) * 0.05 validation : [value] >= 0 && [value] <= 12.5 when : always uom : kPa flags : none
Keyswitch Battery Potential / Battery Potential (Voltage) Switched | 2 | 7020016917 |  | FEF701 | FFFFFFFFFFFF0B10 | 205.35 V | Pass |  | sources : 1 0 pgn : 65271 spn : 158 offset : 7-8 translation : (([value] >> 48) & 0xffffUL) * 0.05 validation : [value] >= 0 && [value] <= 3212.75 when : always uom : V flags : none
Battery Potential / Power Input 1 / Electrical Potential (Voltage) | 2 | 7020016917 |  | FEF701 | FFFFFFFFA720FFFF | 417.95 V | Pass |  | sources : 1 0 pgn : 65271 spn : 168 offset : 5-6 translation : (([value] >> 32) & 0xffffUL) * 0.05 validation : [value] >= 0 && [value] <= 3212.75 when : always uom : V flags : none
Alternator Current | 2 | 7020016917 |  | FEF701 | FF1BFFFFFFFFFFFF | 27 A | Pass |  | sources : 1 0 pgn : 65271 spn : 115 offset : 2 translation : ([value] >> 8) & 0xffUL validation : [value] >= 0 && [value] <= 250 when : always uom : A flags : none
Charging System Potential (Voltage) | 2 | 7020016917 |  | FEF701 | FFFF3A0CFFFFFFFF | 156.5 V | Pass |  | sources : 1 0 pgn : 65271 spn : 167 offset : 3-4 translation : (([value] >> 16) & 0xffffUL) * 0.05 validation : [value] >= 0 && [value] <= 3212.75 when : always uom : V flags : none
Engine Gas Supply Pressure / Engine Gaseous Fuel Supply Pressure | 2 | 7020016917 |  | FEFD01 | FF3A0CFFFFFFFFFF | 1565 kPa | Pass |  | sources : 0 1 pgn : 65277 spn : 159 offset : 2-3 translation : (([value] >> 8) & 0xffffUL) * 0.5 validation : [value] >= 0 && [value] <= 32127.5 when : always uom : kPa flags : none
Total Fuel Used (Gaseous) | 2 | 7020016917 |  | FEAF01 | FFFFFFFF14010C37 | 461766794 kg | Pass |  | sources : 0 1 pgn : 65199 spn : 1040 offset : 5-8 translation : (([value] >> 32) & 0xffffffffUL) * 0.5 validation : [value] >= 0 && [value] <= 2105540607.5 when : always uom : kg flags : none
Engine Fuel Filter Differential Pressure | 2 | 7020016917 |  | FEFC00 | FFFF2EFFFFFFFFFF | 92 kPa | Pass |  | sources : 0 pgn : 65276 spn : 95 offset : 3 translation : (([value] >> 16) & 0xffUL) * 2.0 validation : [value] >= 0 && [value] <= 500 when : always uom : kPa flags : none
Engine Oil Filter Differential Pressure | 2 | 7020016917 |  | FEFC00 | FFFFFF2EFFFFFFFF | 23 kPa | Pass |  | sources : 0 pgn : 65276 spn : 99 offset : 4 translation : (([value] >> 24) & 0xffUL) * 0.5 validation : [value] >= 0 && [value] <= 125 when : always uom : kPa flags : none
Engine Total Idle Fuel Used | 2 | 7020016917 |  | FEDC01 | 0A0100B1FFFFFFFF | 1484783749 L | Pass |  | sources : 0 1 pgn : 65244 spn : 236 offset : 1-4 translation : ([value] & 0xffffffffUL) * 0.5 validation : [value] >= 0 && [value] <= 2105540607.5 when : always uom : l flags : none
Engine Total Idle Hours / Engine Idle Time | 2 | 7020016917 |  | FEDC01 | FFFFFFFF0A0100A1 | 135056602.1 hrs | Pass |  | sources : 0 1 pgn : 65244 spn : 235 offset : 5-8 translation : (([value] >> 32) & 0xffffffffUL) * 0.05 validation : [value] >= 0 && [value] <= 210554060.75 when : always uom : hour flags : none
Engine Torque / Actual Engine - Percent Torque | 2 | 7020016917 |  | F00401 | F0007D0000000000 | 0% | Pass |  | sources : 0 1 pgn : 61444 spn : 513 offset : 3 translation : (([value] >> 16) & 0xffUL) -125.0 validation : [value] >= 0 && [value] <= 125 when : always uom : % flags : none
DEF level Isuzu | 2 | 7020016917 |  | FFE801 | 7D00000000000000 | 50% | Pass |  | sources : 0 1 pgn : 65512 spn : 99999 (Data 1) offset : 1 translation : ([value] & 0xffUL) * 0.4 validation : [value] >= 0 && [value] <= 100 when : always uom : % flags : none
Fuel Info 4 Gas | 2 | 7020016917 |  | FCC301 | 409C000000000000 | 100% | Check |  | sources : 0 1 pgn : 64707 spn : 5867 (Data 1-2) offset : 1 translation : ([value] & 0xffffUL) * 0.0025%/bit validation : [value] >= 0 && [value] <= 161 when : always uom : % flags : none
J1939_change_of_state
Description | resource | device.id | snapshot.pgn_id | snapshot.raw.value | expected_value | status | Tc_ref
DPF Active Regen Status | 0 | 7020016917 | FD7C01 | FF00FFFFFFFFFFFF | Regen Not Active | Pass | 0xFD7C (64892) |  | sources : 0 1 pgn : 64892 spn : 3700 offset : 2.3 translation : ([value] >> 10) & 0x3UL validation : [value] >= 0 && [value] <= 3 when : always flags : none
DPF Active Regen Status | 0 | 7020016917 | FD7C01 | FF04FFFFFFFFFFFF | Regen Active | Pass | 0xFD7C (64892)
DPF Active Regen Status | 0 | 7020016917 | FD7C01 | FF08FFFFFFFFFFFF | Regen Imminent | Pass | 0xFD7C (64892)
DPF Active Regen Status | 0 | 7020016917 | FD7C01 | FF0CFFFFFFFFFFFF | N/A | Pass | 0xFD7C (64892)
DPF Status | 0 | 7020016917 | FD7C01 | FF00FFFFFFFFFFFF | Regeneration Not Needed | Pass | 0xFD7C (64892) |  | sources : 0 1 pgn : 64892 spn : 3701 offset : 2.5 translation : ([value] >> 12) & 0x7UL validation : [value] >= 0 && [value] <= 7 when : always flags : none
DPF Status | 0 | 7020016917 | FD7C01 | FF10FFFFFFFFFFFF | Regeneration Needed - Lowest Level | Pass | 0xFD7C (64892)
DPF Status | 0 | 7020016917 | FD7C01 | FF20FFFFFFFFFFFF | Regeneration Needed - Moderate Level | Pass | 0xFD7C (64892)
DPF Status | 0 | 7020016917 | FD7C01 | FF30FFFFFFFFFFFF | Regeneration Needed - Highest Level | Pass | 0xFD7C (64892)
DPF Status | 0 | 7020016917 | FD7C01 | FF70FFFFFFFFFFFF | Not Available | Pass | 0xFD7C (64892)
DPF Regen Inhibited | 0 | 7020016917 | FD7C01 | FFFF00FFFFFFFFFF | Not Inhibited | Pass | 0xFD7C (64892) |  | sources : 0 1 pgn : 64892 spn : 3702 offset : 3.1 translation : ([value] >> 16) & 0x3UL validation : [value] >= 0 && [value] <= 3 when : always flags : none
DPF Regen Inhibited | 0 | 7020016917 | FD7C01 | FFFF01FFFFFFFFFF | Inhibited | Pass | 0xFD7C (64892)
DPF Regen Inhibited | 0 | 7020016917 | FD7C01 | FFFF03FFFFFFFFFF | Not Available | Pass | 0xFD7C (64892)
modbus_periodic_16
Onei3 | TU Manager - Insight | TU Manager - Advance Sensor | resource | device.id | event.registers.value | snapshot.slaveAddress | snapshot.type | snapshot.address | snapshot.registers.registers | expecetd.value | status | Comments |  | Package Details:
Oil Pressure |  |  | 2 | 7020016917 | 0,0,4199,12767,2974619,0,24 | 10 | 4 | 1024 | 8 | 8 kPa | Pass
Coolant Temp |  |  | 2 | 7020016917 | 0,0,4199,12767,2974619,0,24 | 10 | 4 | 1025 | 12 | -38 C | Pass
Oil Temp |  |  | 2 | 7020016917 | 0,0,4199,12767,2974619,0,24 | 10 | 4 | 1026 | 0 | -50 C | Pass
Fuel Level | Fuel Level |  | 2 | 7020016917 | 0,0,4199,12767,2974619,0,24 | 10 | 4 | 1027 | 0 | 0% | Pass |  |  | slave : 10 registerType : holdingRegister address : 1027 translation : uint16be([value_raw],1) * 1.0 validation : [value] >= 0 && [value] <= 100 uom : % flags : none
Charge Alternator Voltage |  |  | 2 | 7020016917 | 0,0,4199,12767,2974619,0,24 | 10 | 4 | 1028 | 5 | 5 V | Pass
Reserved |  |  | 2 | 7020016917 | 0,0,4199,12767,2974619,0,24 | 10 | 4 | 1029 | 0 |  | Pass
Engine Speed |  |  | 2 | 7020016917 | 0,0,4199,12767,2974619,0,24 | 10 | 4 | 1030 | 10 | 10 rpm | Pass
Frequency |  | Tank Fresh Water | 2 | 7020016917 | 0,0,4199,12767,2974619,0,24 | 10 | 4 | 1031 | 20 | 2hz | Pass |  |  | slave : 10 registerType : holdingRegister address : 1031 translation : uint16be([value_raw],1) * 0.1 validation : [value] >= 0 && [value] <= 70 uom : hz flags : none
Total Power Factor | AC Total Power Factor |  | 2 | 7020016917 | 0,0,4199,12767,2974619,0,24 | 10 | 4 | 1557 | 1 | 0.01 | Pass |  |  | slave : 10 registerType : holdingRegister address : 1557 translation : sint16be([value_raw],1) == 32765 ? 0 : sint16be([value_raw],1) * 0.01 flags : none
Percent kW |  | Percent kW | 2 | 7020016917 | 0,0,4199,12767,2974619,0,24 | 10 | 4 | 1558 | 50 | 5% | Pass |  |  | slave : 10 registerType : holdingRegister address : 1558 translation : sint16be([value_raw],1) * 0.1 validation : [value] >= 0 && [value] <= 100 uom : % flags : none
DEF Level |  |  | 2 | 7020016917 | 0,0,4199,12767,2974619,0,24 | 10 | 4 | 1471 | 7 | 7% | Pass
modbus_periodic_32
Onei3 | TU Manager - Insight | TU Manager - Advance Sensor | resource | device.id | event.registers.value | snapshot.slaveAddress | snapshot.type | snapshot.address | snapshot.registers.registers.H | snapshot.registers.registers.L | expecetd.value | status | Comments
Phase A L-N Voltage | AC Phase L1 Neutral RMS Voltage |  | 2 | 7020016917 | 0,0,4199,12767,2974619,0,24 | 10 | 4 | 1032 | 0 | 40 | 4 V | Pass |  | slave : 10 registerType : holdingRegister address : 1032 translation : uint32be([value_raw],1) == 4294967295 ? 0 : uint32be([value_raw],1) * 0.1 uom : V flags : none
Phase B L-N Voltage | AC Phase L2 Neutral RMS Voltage |  | 2 | 7020016917 | 0,0,4199,12767,2974619,0,24 | 10 | 4 | 1034 | 0 | 60 | 6 V | Pass |  | slave : 10 registerType : holdingRegister address : 1034 translation : uint32be([value_raw],1) == 4294967295 ? 0 : uint32be([value_raw],1) * 0.1 uom : V flags : none
Phase C L-N Voltage | AC Phase L3 Neutral RMS Voltage |  | 2 | 7020016917 | 0,0,4199,12767,2974619,0,24 | 10 | 4 | 1036 | 0 | 80 | 8 V | Pass |  | slave : 10 registerType : holdingRegister address : 1036 translation : uint32be([value_raw],1) == 4294967295 ? 0 : uint32be([value_raw],1) * 0.1 uom : V flags : none
Phase A-B Voltage | AC Phase L1-L2 RMS Voltage |  | 2 | 7020016917 | 0,0,4199,12767,2974619,0,24 | 10 | 4 | 1038 | 0 | 100 | 10 V | Pass |  | slave : 10 registerType : holdingRegister address : 1038 translation : uint32be([value_raw],1) == 4294967295 ? 0 : uint32be([value_raw],1) * 0.1 uom : V flags : none
Phase B-C Voltage |  | Generator Phase BC Voltage | 2 | 7020016917 | 0,0,4199,12767,2974619,0,24 | 10 | 4 | 1040 | 0 | 120 | 12 V | Pass |  | slave : 10 registerType : holdingRegister address : 1040 translation : uint32be([value_raw],1) == 4294967295 ? 0 : uint32be([value_raw],1) * 0.1 uom : V flags : none
Phase C-A Voltage | AC Phase L3-L1 RMS Voltage |  | 2 | 7020016917 | 0,0,4199,12767,2974619,0,24 | 10 | 4 | 1042 | 0 | 140 | 14 V | Pass |  | slave : 10 registerType : holdingRegister address : 1042 translation : uint32be([value_raw],1) == 4294967295 ? 0 : uint32be([value_raw],1) * 0.1 uom : V flags : none
Phase A Current | AC Phase L1 RMS Current |  | 2 | 7020016917 | 0,0,4199,12767,2974619,0,24 | 10 | 4 | 1044 | 0 | 160 | 16 A | Pass |  | slave : 10 registerType : holdingRegister address : 1044 translation : uint32be([value_raw],1) == 4294967295 ? 0 : uint32be([value_raw],1) * 0.1 uom : A flags : none
Phase B Current | AC Phase L2 RMS Current |  | 2 | 7020016917 | 0,0,4199,12767,2974619,0,24 | 10 | 4 | 1046 | 0 | 180 | 18 A | Pass |  | slave : 10 registerType : holdingRegister address : 1046 translation : uint32be([value_raw],1) == 4294967295 ? 0 : uint32be([value_raw],1) * 0.1 uom : A flags : none
Phase C Current | AC Phase L3 RMS Current |  | 2 | 7020016917 | 0,0,4199,12767,2974619,0,24 | 10 | 4 | 1048 | 0 | 200 | 20 A | Pass |  | slave : 10 registerType : holdingRegister address : 1048 translation : uint32be([value_raw],1) == 4294967295 ? 0 : uint32be([value_raw],1) * 0.1 uom : A flags : none
Total kW -- Total Real Power |  |  | 2 | 7020016917 | 0,0,4199,12767,2974619,0,24 | 10 | 4 | 1536 | 0 | 500 | 0.50 kW | Pass |  | slave : 10 registerType : holdingRegister address : 1536 translation : sint32be([value_raw],1) * 0.001 validation : [value] >= 0 && [value] <= 50000000 uom : kW flags : none
Total kVA -- Total Apparent Power |  |  | 2 | 7020016917 | 0,0,4199,12767,2974619,0,24 | 10 | 4 | 1544 | 0 | 600 | 0.60 kVA | Pass |  | slave : 10 registerType : holdingRegister address : 1544 translation : sint32be([value_raw],1) * 0.001 validation : [value] >= 0 && [value] <= 1000000 uom : kVA flags : none
Total kVAR -- Total Reactive Power |  |  | 2 | 7020016917 | 0,0,4199,12767,2974619,0,24 | 10 | 4 | 1552 | 0 | 700 | 0.70 kVAR | Pass |  | slave : 10 registerType : holdingRegister address : 1552 translation : sint32be([value_raw],1) * 0.001 validation : [value] >= 0 && [value] <= 1000000 uom : kVAR flags : none
Average L-L Voltage | Average AC Phase to Phase RMS Voltage |  | 2 | 7020016917 | 0,0,4199,12767,2974619,0,24 | 10 | 4 | 1658 | 0 | 150 | 15 V | Pass |  | slave : 10 registerType : holdingRegister address : 1658 translation : uint32be([value_raw],1) == 4294967295 ? 0 : uint32be([value_raw],1) * 0.1 uom : V flags : none
Average L-N Voltage | Average AC Phase to Neutral RMS Voltage |  | 2 | 7020016917 | 0,0,4199,12767,2974619,0,24 | 10 | 4 | 1650 | 0 | 300 | 30 V | Pass |  | slave : 10 registerType : holdingRegister address : 1650 translation : uint32be([value_raw],1) == 4294967295 ? 0 : uint32be([value_raw],1) * 0.1 uom : V flags : none
Average Current | Average AC RMS Current |  | 2 | 7020016917 | 0,0,4199,12767,2974619,0,24 | 10 | 4 | 1666 | 0 | 1000 | 100 A | Pass |  | slave : 10 registerType : holdingRegister address : 1666 translation : uint32be([value_raw],1) == 4294967295 ?0 : uint32be([value_raw],1) * 0.1 uom : A flags : none
Run Hours | Cumulative Operating Hours - Live Status |  | 2 | 7020016917 | 0,0,4199,12767,2974619,0,24 | 10 | 4 | 1798 | 0 | 7200 | 2 hrs | Pass |  | slave : 10 registerType : holdingRegister address : 1798 translation : uint32be([value_raw],1) * 0.000277778 validation : [value] >= 0 && [value] <= 4290000000 uom : h flags : none
modbus_change_of_state
Description | resource | device.id | snapshot.slaveAddress | snapshot.type | snapshot.address | snapshot.registers.registers | expecetd.value | status | Comments
Control Panel Mode-DSE | 0 | 7020016917 | 10 | 4 | 772 | 0 | Stop | Pass |  |  |  | dse_ctrl_stat: slave : 10 registerType : holdingRegister address : 772 translation : [value] & 0xf validation : [value] >= 0 && [value] <= 15 flags : none
Control Panel Mode-DSE | 0 | 7020016917 | 10 | 4 | 772 | 1 | Auto | Pass
Control Panel Mode-DSE | 0 | 7020016917 | 10 | 4 | 772 | 2 | Manual | Pass
Control Panel Mode-DSE | 0 | 7020016917 | 10 | 4 | 772 | 3 | Manual | Pass
Control Panel Mode-DSE | 0 | 7020016917 | 10 | 4 | 772 | 4 | Manual | Pass
Control Panel Mode-DSE | 0 | 7020016917 | 10 | 4 | 772 | 5 | Manual | Pass
Control Panel Mode-DSE | 0 | 7020016917 | 10 | 4 | 772 | 6 | Manual | Pass
Control Panel Mode-DSE | 0 | 7020016917 | 10 | 4 | 772 | 7 | Off | Pass
Control Panel Mode-DSE | 0 | 7020016917 | 10 | 4 | 772 | 8 | Manual | Pass
Control Panel Mode-DSE | 0 | 7020016917 | 10 | 4 | 772 | 9 | Manual | Pass
Control Panel Mode-DSE | 0 | 7020016917 | 10 | 4 | 772 | 10 | Manual | Pass
Control Panel Mode-DSE | 0 | 7020016917 | 10 | 4 | 772 | 11 | Manual | Pass
Control Panel Mode-DSE | 0 | 7020016917 | 10 | 4 | 772 | 12 | Manual | Pass
Control Panel Mode-DSE | 0 | 7020016917 | 10 | 4 | 772 | 13 | Manual | Pass
Control Panel Mode-DSE | 0 | 7020016917 | 10 | 4 | 772 | 14 | Manual | Pass
Control Panel Mode-DSE | 0 | 7020016917 | 10 | 4 | 772 | 15 | Manual | Pass
Emergency Stop Alarm | 0 | 7020016917 | 10 | 4 | 39425 | 0 | Ok | Pass |  |  |  | slave : 10 registerType : holdingRegister address : 39425 translation : ([value] >> 12) & 0xf validation : [value] >= 0 && [value] <= 15 flags : none
Emergency Stop Alarm | 0 | 7020016917 | 10 | 4 | 39425 | 4096 | Ok | Pass
Emergency Stop Alarm | 0 | 7020016917 | 10 | 4 | 39425 | 8192 | Warning | Pass
Emergency Stop Alarm | 0 | 7020016917 | 10 | 4 | 39425 | 12288 | Shutdown | Pass
Emergency Stop Alarm | 0 | 7020016917 | 10 | 4 | 39425 | 16384 | Shutdown | Pass
Emergency Stop Alarm | 0 | 7020016917 | 10 | 4 | 39425 | 20480 | Ok | Pass
Emergency Stop Alarm | 0 | 7020016917 | 10 | 4 | 39425 | 24576 | Ok | Pass
Emergency Stop Alarm | 0 | 7020016917 | 10 | 4 | 39425 | 28672 | Ok | Pass
Emergency Stop Alarm | 0 | 7020016917 | 10 | 4 | 39425 | 32768 | Ok | Pass
Emergency Stop Alarm | 0 | 7020016917 | 10 | 4 | 39425 | 36864 | Ok | Pass
Emergency Stop Alarm | 0 | 7020016917 | 10 | 4 | 39425 | 40960 | Warning | Pass
Emergency Stop Alarm | 0 | 7020016917 | 10 | 4 | 39425 | 45056 | Ok | Pass
Emergency Stop Alarm | 0 | 7020016917 | 10 | 4 | 39425 | 49152 | Ok | Pass
Emergency Stop Alarm | 0 | 7020016917 | 10 | 4 | 39425 | 53248 | Ok | Pass
Emergency Stop Alarm | 0 | 7020016917 | 10 | 4 | 39425 | 57344 | Ok | Pass
Emergency Stop Alarm | 0 | 7020016917 | 10 | 4 | 39425 | 61440 | Ok | Pass
Under Frequency | 0 | 7020016917 | 10 | 4 | 39426 | 0 | Ok | Pass |  |  |  | slave : 10 registerType : holdingRegister address : 39426 translation : ([value] >> 4) & 0xf validation : [value] >= 0 && [value] <= 15 flags : none
Under Frequency | 0 | 7020016917 | 10 | 4 | 39426 | 16 | Ok | Pass
Under Frequency | 0 | 7020016917 | 10 | 4 | 39426 | 32 | Warning | Pass
Under Frequency | 0 | 7020016917 | 10 | 4 | 39426 | 48 | Shutdown | Pass
Under Frequency | 0 | 7020016917 | 10 | 4 | 39426 | 64 | Shutdown | Pass
Under Frequency | 0 | 7020016917 | 10 | 4 | 39426 | 80 | Ok | Pass
Under Frequency | 0 | 7020016917 | 10 | 4 | 39426 | 96 | Ok | Pass
Under Frequency | 0 | 7020016917 | 10 | 4 | 39426 | 112 | Ok | Pass
Under Frequency | 0 | 7020016917 | 10 | 4 | 39426 | 128 | Ok | Pass
Under Frequency | 0 | 7020016917 | 10 | 4 | 39426 | 144 | Ok | Pass
Under Frequency | 0 | 7020016917 | 10 | 4 | 39426 | 160 | Warning | Pass
Under Frequency | 0 | 7020016917 | 10 | 4 | 39426 | 176 | Ok | Pass
Under Frequency | 0 | 7020016917 | 10 | 4 | 39426 | 192 | Ok | Pass
Under Frequency | 0 | 7020016917 | 10 | 4 | 39426 | 208 | Ok | Pass
Under Frequency | 0 | 7020016917 | 10 | 4 | 39426 | 224 | Ok | Pass
Under Frequency | 0 | 7020016917 | 10 | 4 | 39426 | 240 | Ok | Pass
Over Frequency | 0 | 7020016917 | 10 | 4 | 39426 | 0 | Ok | Pass |  |  |  | slave : 10 registerType : holdingRegister address : 39426 translation : [value] & 0xf validation : [value] >= 0 && [value] <= 15 flags : none
Over Frequency | 0 | 7020016917 | 10 | 4 | 39426 | 1 | Ok | Pass
Over Frequency | 0 | 7020016917 | 10 | 4 | 39426 | 2 | Warning | Pass
Over Frequency | 0 | 7020016917 | 10 | 4 | 39426 | 3 | Shutdown | Pass
Over Frequency | 0 | 7020016917 | 10 | 4 | 39426 | 4 | Shutdown | Pass
Over Frequency | 0 | 7020016917 | 10 | 4 | 39426 | 5 | Ok | Pass
Over Frequency | 0 | 7020016917 | 10 | 4 | 39426 | 6 | Ok | Pass
Over Frequency | 0 | 7020016917 | 10 | 4 | 39426 | 7 | Ok | Pass
Over Frequency | 0 | 7020016917 | 10 | 4 | 39426 | 8 | Ok | Pass
Over Frequency | 0 | 7020016917 | 10 | 4 | 39426 | 9 | Ok | Pass
Over Frequency | 0 | 7020016917 | 10 | 4 | 39426 | 10 | Warning | Pass
Over Frequency | 0 | 7020016917 | 10 | 4 | 39426 | 11 | Ok | Pass
Over Frequency | 0 | 7020016917 | 10 | 4 | 39426 | 12 | Ok | Pass
Over Frequency | 0 | 7020016917 | 10 | 4 | 39426 | 13 | Ok | Pass
Over Frequency | 0 | 7020016917 | 10 | 4 | 39426 | 14 | Ok | Pass
Over Frequency | 0 | 7020016917 | 10 | 4 | 39426 | 15 | Ok | Pass
Low AC Voltage | 0 | 7020016917 | 10 | 4 | 39427 | 0 | Ok | Pass |  |  |  | slave : 10 registerType : holdingRegister address : 39427 translation : ([value] >> 12) & 0xf validation : [value] >= 0 && [value] <= 15 flags : none
Low AC Voltage | 0 | 7020016917 | 10 | 4 | 39427 | 4096 | Ok | Pass
Low AC Voltage | 0 | 7020016917 | 10 | 4 | 39427 | 8192 | Warning | Pass
Low AC Voltage | 0 | 7020016917 | 10 | 4 | 39427 | 12288 | Shutdown | Pass
Low AC Voltage | 0 | 7020016917 | 10 | 4 | 39427 | 16384 | Shutdown | Pass
Low AC Voltage | 0 | 7020016917 | 10 | 4 | 39427 | 20480 | Ok | Pass
Low AC Voltage | 0 | 7020016917 | 10 | 4 | 39427 | 24576 | Ok | Pass
Low AC Voltage | 0 | 7020016917 | 10 | 4 | 39427 | 28672 | Ok | Pass
Low AC Voltage | 0 | 7020016917 | 10 | 4 | 39427 | 32768 | Ok | Pass
Low AC Voltage | 0 | 7020016917 | 10 | 4 | 39427 | 36864 | Ok | Pass
Low AC Voltage | 0 | 7020016917 | 10 | 4 | 39427 | 40960 | Warning | Pass
Low AC Voltage | 0 | 7020016917 | 10 | 4 | 39427 | 45056 | Ok | Pass
Low AC Voltage | 0 | 7020016917 | 10 | 4 | 39427 | 49152 | Ok | Pass
Low AC Voltage | 0 | 7020016917 | 10 | 4 | 39427 | 53248 | Ok | Pass
Low AC Voltage | 0 | 7020016917 | 10 | 4 | 39427 | 57344 | Ok | Pass
Low AC Voltage | 0 | 7020016917 | 10 | 4 | 39427 | 61440 | Ok | Pass
High AC Voltage | 0 | 7020016917 | 10 | 4 | 39427 | 0 | Ok | Pass |  |  |  | slave : 10 registerType : holdingRegister address : 39427 translation : ([value] >> 8) & 0xf validation : [value] >= 0 && [value] <= 15 flags : none
High AC Voltage | 0 | 7020016917 | 10 | 4 | 39427 | 256 | Ok | Pass
High AC Voltage | 0 | 7020016917 | 10 | 4 | 39427 | 512 | Warning | Pass
High AC Voltage | 0 | 7020016917 | 10 | 4 | 39427 | 768 | Shutdown | Pass
High AC Voltage | 0 | 7020016917 | 10 | 4 | 39427 | 1024 | Shutdown | Pass
High AC Voltage | 0 | 7020016917 | 10 | 4 | 39427 | 1280 | Ok | Pass
High AC Voltage | 0 | 7020016917 | 10 | 4 | 39427 | 1536 | Ok | Pass
High AC Voltage | 0 | 7020016917 | 10 | 4 | 39427 | 1792 | Ok | Pass
High AC Voltage | 0 | 7020016917 | 10 | 4 | 39427 | 2048 | Ok | Pass
High AC Voltage | 0 | 7020016917 | 10 | 4 | 39427 | 2304 | Ok | Pass
High AC Voltage | 0 | 7020016917 | 10 | 4 | 39427 | 2560 | Warning | Pass
High AC Voltage | 0 | 7020016917 | 10 | 4 | 39427 | 2816 | Ok | Pass
High AC Voltage | 0 | 7020016917 | 10 | 4 | 39427 | 3072 | Ok | Pass
High AC Voltage | 0 | 7020016917 | 10 | 4 | 39427 | 3328 | Ok | Pass
High AC Voltage | 0 | 7020016917 | 10 | 4 | 39427 | 3584 | Ok | Pass
High AC Voltage | 0 | 7020016917 | 10 | 4 | 39427 | 3840 | Ok | Pass
High Current | 0 | 7020016917 | 10 | 4 | 39430 | 0 | Ok | Pass |  |  |  | slave : 10 registerType : holdingRegister address : 39430 translation : ([value] >> 12) & 0xf validation : [value] >= 0 && [value] <= 15 flags : none
High Current | 0 | 7020016917 | 10 | 4 | 39430 | 4096 | Ok | Pass
High Current | 0 | 7020016917 | 10 | 4 | 39430 | 8192 | Warning | Pass
High Current | 0 | 7020016917 | 10 | 4 | 39430 | 12288 | Shutdown | Pass
High Current | 0 | 7020016917 | 10 | 4 | 39430 | 16384 | Shutdown | Pass
High Current | 0 | 7020016917 | 10 | 4 | 39430 | 20480 | Ok | Pass
High Current | 0 | 7020016917 | 10 | 4 | 39430 | 24576 | Ok | Pass
High Current | 0 | 7020016917 | 10 | 4 | 39430 | 28672 | Ok | Pass
High Current | 0 | 7020016917 | 10 | 4 | 39430 | 32768 | Ok | Pass
High Current | 0 | 7020016917 | 10 | 4 | 39430 | 36864 | Ok | Pass
High Current | 0 | 7020016917 | 10 | 4 | 39430 | 40960 | Warning | Pass
High Current | 0 | 7020016917 | 10 | 4 | 39430 | 45056 | Ok | Pass
High Current | 0 | 7020016917 | 10 | 4 | 39430 | 49152 | Ok | Pass
High Current | 0 | 7020016917 | 10 | 4 | 39430 | 53248 | Ok | Pass
High Current | 0 | 7020016917 | 10 | 4 | 39430 | 57344 | Ok | Pass
High Current | 0 | 7020016917 | 10 | 4 | 39430 | 61440 | Ok | Pass
kW Overload | 0 | 7020016917 | 10 | 4 | 39432 | 0 | Ok | Pass |  |  |  | slave : 10 registerType : holdingRegister address : 39432 translation : ([value] >> 4) & 0xf validation : [value] >= 0 && [value] <= 15 flags : none
kW Overload | 0 | 7020016917 | 10 | 4 | 39432 | 16 | Ok | Pass
kW Overload | 0 | 7020016917 | 10 | 4 | 39432 | 32 | Warning | Pass
kW Overload | 0 | 7020016917 | 10 | 4 | 39432 | 48 | Shutdown | Pass
kW Overload | 0 | 7020016917 | 10 | 4 | 39432 | 64 | Shutdown | Pass
kW Overload | 0 | 7020016917 | 10 | 4 | 39432 | 80 | Ok | Pass
kW Overload | 0 | 7020016917 | 10 | 4 | 39432 | 96 | Ok | Pass
kW Overload | 0 | 7020016917 | 10 | 4 | 39432 | 112 | Ok | Pass
kW Overload | 0 | 7020016917 | 10 | 4 | 39432 | 128 | Ok | Pass
kW Overload | 0 | 7020016917 | 10 | 4 | 39432 | 144 | Ok | Pass
kW Overload | 0 | 7020016917 | 10 | 4 | 39432 | 160 | Warning | Pass
kW Overload | 0 | 7020016917 | 10 | 4 | 39432 | 176 | Ok | Pass
kW Overload | 0 | 7020016917 | 10 | 4 | 39432 | 192 | Ok | Pass
kW Overload | 0 | 7020016917 | 10 | 4 | 39432 | 208 | Ok | Pass
kW Overload | 0 | 7020016917 | 10 | 4 | 39432 | 224 | Ok | Pass
kW Overload | 0 | 7020016917 | 10 | 4 | 39432 | 240 | Ok | Pass
Common Alarm Status | 0 | 7020016917 | 10 | 4 | 774 | 0 | Ok | Check |  |  |  | slave : 10 registerType : holdingRegister address : 774 translation : (([value] >> 10) < 1025 && ([value] >> 10) >= 1024 ? 1 :([value] >> 10) < 2049 && ([value] >> 10) >= 2048 ? 2 :([value] >> 10) < 32769 && ([value] >> 10) >= 4096 ? 3 :([value] >> 10)) & 0x7 validation : [value] >= 0 && [value] <= 32768 flags : none
Common Alarm Status | 0 | 7020016917 | 10 | 4 | 774 | 1 | Warning | Check
Common Alarm Status | 0 | 7020016917 | 10 | 4 | 774 | 2 | Electrical Trip | Check
Common Alarm Status | 0 | 7020016917 | 10 | 4 | 774 | 3 | - | Check
Common Alarm Status | 0 | 7020016917 | 10 | 4 | 774 | 4 | Shutdown | Check
Common Alarm Status | 0 | 7020016917 | 10 | 4 | 774 | 5 | Shutdow/Warn | Check
Common Alarm Status | 0 | 7020016917 | 10 | 4 | 774 | 6 | Shutdow/Elec Trip | Check
Common Alarm Status | 0 | 7020016917 | 10 | 4 | 774 | 7 | Total Failure | Check
Common Alarm Status | 0 | 7020016917 | 10 | 4 | 774 | 8 | - | Check
Common Alarm Status | 0 | 7020016917 | 10 | 4 | 774 | 9 | - | Check
Common Alarm Status | 0 | 7020016917 | 10 | 4 | 774 | 10 | - | Check
Common Alarm Status | 0 | 7020016917 | 10 | 4 | 774 | 11 | - | Check
Common Alarm Status | 0 | 7020016917 | 10 | 4 | 774 | 12 | - | Check
Common Alarm Status | 0 | 7020016917 | 10 | 4 | 774 | 13 | - | Check
Common Alarm Status | 0 | 7020016917 | 10 | 4 | 774 | 14 | - | Check
Common Alarm Status | 0 | 7020016917 | 10 | 4 | 774 | 15 | - | Check
Engine Status | 0 | 7020016917 | 10 | 4 | 48640 | 0 | Off | Check |  |  |  | code : 22000 translation : false flags : filterDuplicates code : 22001 translation : true flags : filterDuplicates
Engine Status | 0 | 7020016917 | 10 | 4 | 48640 | 1 | On | Check
Payloads:
J1939: No | 120908ebbedb990610d10220002a003a02100b1814583
J1939: Yes | 1205082d10fa0420012a003a02100b18145835
Modbus: No | 120908a0bfdb990610ef062000181e5820
Modbus: Yes | 120608940510c1072001181e5820
Device:
7010102722
7020016917

## j1939_periodic_demo
Onei3 | TU Manager - Insight | TU Manager - Advance Sensor | resource | device.id | event.registers.value | snapshot.pgn_id | snapshot.raw.value | expecetd.value | status | Comments
Engine Speed | Engine Speed |  | 2 | 7020016917 | 0,0,4199,12767,2974619,0,24 | F00401 | FFFFFFA10FFFFFFF | 500.13 rpm
DEF level Isuzu |  |  | 2 | 7020016917 |  | FFE801 | 7D00000000000000 | 50%
Diesel Particulate Filter 1 Time Since Last Active Regeneration |  |  | 2 | 7020016917 |  | FD7B01 | FFFF09B0A100FFFF | 122.64 Days
Engine Coolant Temperature | Engine Coolant Temperature |  | 2 | 7020016917 |  | FEEE01 | B1FFFFFFFFFFFFFF | (177-40) = 137 deg C
Alternator Current |  | Tank Black (Waste) | 2 | 7020016917 |  | FEF701 | FF1BFFFFFFFFFFFF | 27 A
Charging System Potential (Voltage) |  |  | 2 | 7020016917 |  | FEF701 | FFFF3A0CFFFFFFFF | 156.5 V
Engine Gas Supply Pressure |  | Tank Oil | 2 | 7020016917 |  | FEFD01 | FF3A0CFFFFFFFFFF | 1565 kPa
Total Fuel Used (Gaseous) |  | Tank Fuel | 2 | 7020016917 |  | FEAF01 | FFFFFFFF14010C37 | 461766794 kg
Fuel Info 4 Gas |  |  | 2 | 7020016917 |  | FCC301 | B04F0000000000000 | 51%
Time to Next Active Regeneration |  |  | 2 | 7020016917 |  | FCB901 | 1700A108FFFFFFFF | 1675.56 days | Not Found
Time Since Last System Cleaning Event |  |  | 2 | 7020016917 |  | FCB901 | FFFFFFFF0A610101 | 195.22 days | Not Found
Ambient Air Temperature |  |  | 2 | 7020016917 |  | FEF501 | FFFFFFC30AFFFFFF | 86.09375 deg C | Not Found
Engine Exhaust Gas Temperature |  |  | 2 | 7020016917 |  | FEF601 | FFFFFFFFFF0B10FF | 128.34375 deg C | Not Found
Supply Gas Methane Percentage |  |  | 2 | 7020016917 |  | FEFC01 | D01BFFFFFFFFFFFF | 0.178 | Not Found
Gaseous Engine Run Hours |  |  | 2 | 7020016917 |  | FCA001 | 0A0100B1FFFFFFFF | 148478374.9 hrs | Not Found
Diesel Engine Run Hours |  |  | 2 | 7020016917 |  | FCA001 | FFFFFFFF0A010011 | 14260646.9 hrs | Not Found
Engine Gaseous Fuel Supply Unit Intake Pressure |  |  | 2 | 7020016917 |  | FC3A01 | FFFFA720FFFFFFFF | 4179.5 kPa | Not Found
Engine Total Gaseous Fuel Volume Used |  |  | 2 | 7020016917 |  | FC1101 | 0A0100B1FFFFFFFF | 1484783749 m^3 | Not Found
Engine Total Gaseous Idle Fuel Volume Used |  |  | 2 | 7020016917 |  | FC1101 | FFFFFFFF0A010011 | 142606469 m^3 | Not Found

## modbus_periodic_16_demo
Description | resource | device.id | event.registers.value | snapshot.slaveAddress | snapshot.type | snapshot.address | snapshot.registers.registers | expecetd.value | status | Comments
Fuel Level | 2 | 7020016917 | 0,0,4199,12767,2974619,0,24 | 10 | 4 | 1027 | 70 |  | Pass | 0 --> 0% 50 --> 50% 70 --> 70%

## modbus_periodic_32_demo
Description | resource | device.id | event.registers.value | snapshot.slaveAddress | snapshot.type | snapshot.address | snapshot.registers.registers.H | snapshot.registers.registers.L | expecetd.value | status | Comments
Run Hours | 2 | 7020016917 | 0,0,4199,12767,2974619,0,24 | 10 | 4 | 1798 | 0 | 19800 |  | Pass | 0 --> 0hrs 7200 --> 2hrs 19800 --> 5.5 hrs

## modbus_change_of_state_demo
Description | resource | device.id | snapshot.slaveAddress | snapshot.type | snapshot.address | snapshot.registers.registers | expected_value | Status | Tc_ref
Control Panel Mode-DSE | 0 | 7020016917 | 10 | 4 | 772 | 0 |  | Pass | 0 --> Stop 1 --> Auto

## j1939_change_of_state_demo
Description | resource | device.id | snapshot.pgn_id | snapshot.raw.value | expected_value | status | Tc_ref | comments
DPF Active Regen Status | 0 | 7020016917 | FD7C01 | FF0400FFFFFFFFFF |  | Pass | 0xFD7C (64892) | FF0000FFFFFFFFFF -->Regen Not Active FF0400FFFFFFFFFF -->Regen Active FF0800FFFFFFFFFF -->Regen Imminent FF0C00FFFFFFFFFF -->N/A

## gps_fix
description | resource | device.id | event.location.type | event.location.quality | event.location.latitude | expected_latitude | event.location.longitude | expected_longitude | event.location.altitude_m | event.location.heading_deg | event.modem.rsrp | event.modem.technology | event.physical_io.inputs | event.registers.value.extend | event.blocktype
Location | 0 | 7020016917 | VALID_3D | GOOD | 483321133 | 42.9321 | -792040374 | -81.204 | 210 | 140 | -90 | NET_4G | 9 | 0, 6, 4190, 11661, 11465553, 18, 18 | 279

## resource_2
description | resource | device.id | event.registers.value | snapshot.pgn_id | snapshot.raw.value | expected_value
Engine Total Fuel Used | 2 | 7020016917 | 0,6,4176, 13938,1959872,270,8 | FEE901 | 0000000011111111 | 143165576.5
Fuel Level 1 | 2 | 7020016917 | 0,6,4176, 13938,1959872,270,8 | FEFC01 | FF24FFFFFFFFFFFF | 40

## j1939_threshold
description | resource | sample_payload | device.id | snapshot.pgn_id | snapshot.raw.value | expected_value
Engine Run Status (RPM based) | 0 | 120808befa959a0610321a021004220518990140032a021009320e120c0000e720df639bc7b50100183a11188188c007220a1a08ffffffa10fffffff409702 | 7020016917 | F00401 | FFFFFFA10FFFFFFF | 500.13 rpm

## physical_io_change_of_state
Description | resource | device.id | event.physical_io.inputs | event.registers.value | expected_value
Battery - 12.18V | 0 | 7020016917 | 11 | 0,6,4176, 12183,1431436,40,74840 | 12.18 V
Key Switch Status - On | 0 | 7020016917 | 11 | 0,6,4176, 12183,1431436,40,74840 | On

## j1939_periodic
Onei3 | TU_Manager_Insight | TU_Manager_Advance_Sensor | resource | device.id | event.registers.value | snapshot.pgn_id | snapshot.raw.value | expected_value | status | Comments
Engine Speed | Engine Speed |  | 2 | 7010102722 | 0,0,4199,12767,2974619,0,24 | F01401 | FFFFFFA10FFFFFFF | 500.13 rpm | Pass
Fuel Info 4 Gas -- Supply Gas Methane Percentage |  |  | 2 | 7010102722 |  | FCC301 | D070000000000000 | 50% | Check
DEF level Isuzu |  |  | 2 | 7010102722 |  | FFE801 | 7D00000000000000 | 50% | Pass
Engine Load | Engine Percent Load At Current Speed |  | 2 | 7010102722 |  | F01301 | FFFF34FFFFFFFFFF | 52% | Pass
Diesel Particulate Filter 1 Soot Load Percent | Aftertreatment Diesel Particulate Filter Soot Load Percent |  | 2 | 7010102722 |  | FD7B01 | A7FFFFFFFFFFFFFF | 167% | Pass
Diesel Particulate Filter 1 Ash Load Percent | Aftertreatment Diesel Particulate Filter Ash Load Percent |  | 2 | 7010102722 |  | FD7B01 | FF0BFFFFFFFFFFFF | 11% | Pass
Diesel Particulate Filter 1 Time Since Last Active Regeneration |  |  | 2 | 7010102722 |  | FD7B01 | FFFF09B0A100FFFF | 122.64 Days | Pass
DEF / Aftertreatment 1 SCR Catalyst Tank Level | DEF Tank Level |  | 2 | 7010102722 |  | FE5601 | CBFFFFFFFFFFFFFF | 81.2% | Pass
Engine Total Fuel Used | Fuel Used (total) |  | 2 | 7010102722 |  | FEE901 | FFFFFFFF0A0100A1 | 1350566021 L | Pass
Engine Coolant Temperature | Engine Coolant Temperature |  | 2 | 7010102722 |  | FEEE01 | B1FFFFFFFFFFFFFF | (177-40) = 137 deg C | Pass
Engine Oil Temperature 1 | Engine Oil Temperature |  | 2 | 7010102722 |  | FEEE01 | FFFF01CAFFFFFFFF | (1616.03125 - 237) = 1343.03 deg C | Pass
Engine Oil Pressure | Engine Oil Pressure |  | 2 | 7010102722 |  | FEEF01 | FFFFFF1EFFFFFFFF | 120 kPa | Pass
Engine Fuel Delivery Pressure | Fuel Delivery Pressure |  | 2 | 7010102722 |  | FEEF01 | 4BFFFFFFFFFFFFFF | 300 kPa | Pass
Engine Oil Level | Engine Oil Level |  | 2 | 7010102722 |  | FEEF01 | FFFFD8FFFFFFFFFF | 86.4% | Pass
Engine Coolant Level | Engine Coolant Level |  | 2 | 7010102722 |  | FEEF01 | FFFFFFFFFFFFFFE2 | 90.4% | Pass
Engine Fuel Rate | Fuel Rate |  | 2 | 7010102722 |  | FEF201 | A037FFFFFFFFFFFF | 712 L/h | Pass
Barometric Pressure | Barometric Pressure |  | 2 | 7010102722 |  | FEF501 | D1FFFFFFFFFFFFFF | 104.5 kPa | Pass
Engine Air Inlet Temperature | Engine Intake Air Temperature |  | 2 | 7010102722 |  | FEF501 | FFFFFFFFFF0BFFFF | (11-40) = -29 deg C | Pass
Engine Intake Manifold #1 Pressure | Engine Intake Manifold Pressure |  | 2 | 7010102722 |  | FEF601 | FF1BFFFFFFFFFFFF | 54 kPa | Pass
Engine Intake Manifold 1 Temperature | Engine Intake Manifold Temperature |  | 2 | 7010102722 |  | FEF601 | FFFF5EFFFFFFFFFF | (94 - 40) = 54 deg C | Pass
Engine Air Inlet Pressure | Engine Intake Air Pressure |  | 2 | 7010102722 |  | FEF601 | FFFFFF1CFFFFFFFF | 56 kPa | Pass
Engine Air Filter 1 Differential Pressure | Engine Air Filter Differential Pressure |  | 2 | 7010102722 |  | FEF601 | FFFFFFFF5EFFFFFF | 4.7 kPa | Pass
Keyswitch Battery Potential | Battery Voltage |  | 2 | 7010102722 |  | FEF701 | FFFFFFFFFFFF0B10 | 205.35 V | Pass
Battery Potential / Power Input 1 |  | Battery Potential / Power Input 1 | 2 | 7010102722 |  | FEF701 | FFFFFFFFA720FFFF | 417.95 V | Pass
Alternator Current |  | Tank Black (Waste) | 2 | 7010102722 |  | FEF701 | FF1BFFFFFFFFFFFF | 27 A | Pass
Charging System Potential (Voltage) |  |  | 2 | 7010102722 |  | FEF701 | FFFF3A0CFFFFFFFF | 156.5 V | Pass
Engine Gas Supply Pressure |  | Tank Oil | 2 | 7010102722 |  | FEFD01 | FF3A0CFFFFFFFFFF | 1565 kPa | Pass
Total Fuel Used (Gaseous) |  | Tank Fuel | 2 | 7010102722 |  | FEAF01 | FFFFFFFF14010C37 | 461766794 kg | Pass
Engine Fuel Filter Differential Pressure |  | Engine Fuel Filter Differential Pressure | 2 | 7010102722 |  | FEFC01 | FFFF2EFFFFFFFFFF | 92 kPa | Pass
Engine Oil Filter Differential Pressure |  | Engine Oil Filter Differential Pressure | 2 | 7010102722 |  | FEFC01 | FFFFFF2EFFFFFFFF | 23 kPa | Pass
Engine Total Idle Fuel Used | Fuel used when Idling (total) |  | 2 | 7010102722 |  | FEDC01 | 0A0100B1FFFFFFFF | 1484783749 L | Pass
Engine Idle Time | Total Idle Hours |  | 2 | 7010102722 |  | FEDC01 | FFFFFFFF0A0100A1 | 135056602.1 hrs | Pass
Engine Torque | Actual Engine - Percent Torque |  | 2 | 7010102722 |  | F00401 | F0007DFFFFFFFFFF | 0% | Pass
Time to Next Active Regeneration |  |  | 2 | 7010102722 |  | FCB901 | 1700A108FFFFFFFF | 1675.56 days | Not Found
Time Since Last System Cleaning Event |  |  | 2 | 7010102722 |  | FCB901 | FFFFFFFF0A610101 | 195.22 days | Not Found
Ambient Air Temperature |  |  | 2 | 7010102722 |  | FEF501 | FFFFFFC30AFFFFFF | 86.09375 deg C | Not Found
Engine Exhaust Gas Temperature |  |  | 2 | 7010102722 |  | FEF601 | FFFFFFFFFF0B10FF | 128.34375 deg C | Not Found
Supply Gas Methane Percentage |  |  | 2 | 7010102722 |  | FEFC01 | D01BFFFFFFFFFFFF | 0.178 | Not Found
Gaseous Engine Run Hours |  |  | 2 | 7010102722 |  | FCA001 | 0A0100B1FFFFFFFF | 148478374.9 hrs | Not Found
Diesel Engine Run Hours |  |  | 2 | 7010102722 |  | FCA001 | FFFFFFFF0A010011 | 14260646.9 hrs | Not Found
Engine Gaseous Fuel Supply Unit Intake Pressure |  |  | 2 | 7010102722 |  | FC3A01 | FFFFA720FFFFFFFF | 4179.5 kPa | Not Found
Engine Total Gaseous Fuel Volume Used |  |  | 2 | 7010102722 |  | FC1101 | 0A0100B1FFFFFFFF | 1484783749 m^3 | Not Found
Engine Total Gaseous Idle Fuel Volume Used |  |  | 2 | 7010102722 |  | FC1101 | FFFFFFFF0A010011 | 142606469 m^3 | Not Found

## j1939_change_of_state
Description | resource | device.id | snapshot.pgn_id | snapshot.raw.value | expected_value | status | Tc_ref
DPF Active Regen Status | 0 | 7010102722 | FD7C01 | FF00FFFFFFFFFFFF | Regen Not Active | Pass | 0xFD7C (64892)
DPF Active Regen Status | 0 | 7010102722 | FD7C01 | FF04FFFFFFFFFFFF | Regen Active | Pass | 0xFD7C (64892)
DPF Active Regen Status | 0 | 7010102722 | FD7C01 | FF08FFFFFFFFFFFF | Regen Imminent | Pass | 0xFD7C (64892)
DPF Active Regen Status | 0 | 7010102722 | FD7C01 | FF0CFFFFFFFFFFFF | N/A | Pass | 0xFD7C (64892)
DPF Status | 0 | 7010102722 | FD7C01 | FF00FFFFFFFFFFFF | Regeneration Not Needed | Pass | 0xFD7C (64892)
DPF Status | 0 | 7010102722 | FD7C01 | FF10FFFFFFFFFFFF | Regeneration Needed - Lowest Level | Pass | 0xFD7C (64892)
DPF Status | 0 | 7010102722 | FD7C01 | FF20FFFFFFFFFFFF | Regeneration Needed - Moderate Level | Pass | 0xFD7C (64892)
DPF Status | 0 | 7010102722 | FD7C01 | FF30FFFFFFFFFFFF | Regeneration Needed - Highest Level | Pass | 0xFD7C (64892)
DPF Status | 0 | 7010102722 | FD7C01 | FF70FFFFFFFFFFFF | Not Available | Pass | 0xFD7C (64892)
DPF Regen Inhibited | 0 | 7010102722 | FD7C01 | FFFF00FFFFFFFFFF | Not Inhibited | Pass | 0xFD7C (64892)
DPF Regen Inhibited | 0 | 7010102722 | FD7C01 | FFFF01FFFFFFFFFF | Inhibited | Pass | 0xFD7C (64892)
DPF Regen Inhibited | 0 | 7010102722 | FD7C01 | FFFF03FFFFFFFFFF | Not Available | Pass | 0xFD7C (64892)

## modbus_periodic_16
Onei3 | TU Manager - Insight | TU Manager - Advance Sensor | resource | device.id | event.registers.value | snapshot.slaveAddress | snapshot.type | snapshot.address | snapshot.registers.registers | expecetd.value | status | Comments
Fuel Level | Fuel Level |  | 2 | 7010102722 | 0,0,4199,12767,2974619,0,24 | 10 | 4 | 1027 | 50 | 50% | Pass
Frequency |  | Tank Fresh Water | 2 | 7010102722 | 0,0,4199,12767,2974619,0,24 | 10 | 4 | 1031 | 80 | 8hz | Fail
Total Power Factor | AC Total Power Factor |  | 2 | 7010102722 | 0,0,4199,12767,2974619,0,24 | 10 | 4 | 1557 | 23 | 0.23 | Pass
Total Percent kW |  | Percent kW | 2 | 7010102722 | 0,0,4199,12767,2974619,0,24 | 10 | 4 | 1558 | 250 | 25% | Pass

## modbus_periodic_32
Onei3 | TU Manager - Insight | TU Manager - Advance Sensor | resource | device.id | event.registers.value | snapshot.slaveAddress | snapshot.type | snapshot.address | snapshot.registers.registers.H | snapshot.registers.registers.L | expecetd.value | status | Comments
Phase A L-N Voltage | AC Phase L1 Neutral RMS Voltage |  | 2 | 7010102722 | 0,0,4199,12767,2974619,0,24 | 10 | 4 | 1032 | 0 | 60 | 6 V | Pass
Phase B L-N Voltage | AC Phase L2 Neutral RMS Voltage |  | 2 | 7010102722 | 0,0,4199,12767,2974619,0,24 | 10 | 4 | 1034 | 0 | 80 | 8 V | Pass
Phase C L-N Voltage | AC Phase L3 Neutral RMS Voltage |  | 2 | 7010102722 | 0,0,4199,12767,2974619,0,24 | 10 | 4 | 1036 | 0 | 40 | 4 V | Pass
Phase A-B Voltage | AC Phase L1-L2 RMS Voltage |  | 2 | 7010102722 | 0,0,4199,12767,2974619,0,24 | 10 | 4 | 1038 | 0 | 120 | 12 V | Pass
Phase B-C Voltage |  | Generator Phase BC Voltage | 2 | 7010102722 | 0,0,4199,12767,2974619,0,24 | 10 | 4 | 1040 | 0 | 140 | 14 V | Fail
Phase C-A Voltage | AC Phase L3-L1 RMS Voltage |  | 2 | 7010102722 | 0,0,4199,12767,2974619,0,24 | 10 | 4 | 1042 | 0 | 100 | 10 V | Pass
Phase A Current | AC Phase L1 RMS Current |  | 2 | 7010102722 | 0,0,4199,12767,2974619,0,24 | 10 | 4 | 1044 | 0 | 180 | 18 A | Pass
Phase B Current | AC Phase L2 RMS Current |  | 2 | 7010102722 | 0,0,4199,12767,2974619,0,24 | 10 | 4 | 1046 | 0 | 200 | 20 A | Pass
Phase C Current | AC Phase L3 RMS Current |  | 2 | 7010102722 | 0,0,4199,12767,2974619,0,24 | 10 | 4 | 1048 | 0 | 160 | 16 V | Pass
Total kW -- Total Real Power |  |  | 2 | 7010102722 | 0,0,4199,12767,2974619,0,24 | 10 | 4 | 1536 | 0 | 600 | 0.60 kW | Fail
Total kVA -- Total Apparent Power |  |  | 2 | 7010102722 | 0,0,4199,12767,2974619,0,24 | 10 | 4 | 1544 | 0 | 700 | 0.70 kVA | Fail
Total kVAR -- Total Reactive Power |  |  | 2 | 7010102722 | 0,0,4199,12767,2974619,0,24 | 10 | 4 | 1552 | 0 | 500 | 0.50 kVAR | Fail
Average L-L Voltage | Average AC Phase to Phase RMS Voltage |  | 2 | 7010102722 | 0,0,4199,12767,2974619,0,24 | 10 | 4 | 1658 | 0 | 300 | 30 V | Pass
Average L-N Voltage | Average AC Phase to Neutral RMS Voltage |  | 2 | 7010102722 | 0,0,4199,12767,2974619,0,24 | 10 | 4 | 1650 | 0 | 150 | 15 V | Pass
Average Current | Average AC RMS Current |  | 2 | 7010102722 | 0,0,4199,12767,2974619,0,24 | 10 | 4 | 1666 | 0 | 1050 | 105 A | Pass
Run Hours | Cumulative Operating Hours - Live Status |  | 2 | 7010102722 | 0,0,4199,12767,2974619,0,24 | 10 | 4 | 1798 | 0 | 9000 | 2.5 hrs | Pass

## modbus_change_of_state
Description | resource | device.id | snapshot.slaveAddress | snapshot.type | snapshot.address | snapshot.registers.registers | expected_value | Status | Tc_ref
Control Panel Mode-DSE | 0 | 7010102722 | 10 | 4 | 772 | 0 | Stop | Pass
Control Panel Mode-DSE | 0 | 7010102722 | 10 | 4 | 772 | 1 | Auto | Pass
Control Panel Mode-DSE | 0 | 7010102722 | 10 | 4 | 772 | 2 | Manual | Pass
Control Panel Mode-DSE | 0 | 7010102722 | 10 | 4 | 772 | 3 | Manual | Pass
Control Panel Mode-DSE | 0 | 7010102722 | 10 | 4 | 772 | 4 | Manual | Pass
Control Panel Mode-DSE | 0 | 7010102722 | 10 | 4 | 772 | 5 | Manual | Pass
Control Panel Mode-DSE | 0 | 7010102722 | 10 | 4 | 772 | 6 | Manual | Pass
Control Panel Mode-DSE | 0 | 7010102722 | 10 | 4 | 772 | 7 | Off | Pass
Control Panel Mode-DSE | 0 | 7010102722 | 10 | 4 | 772 | 8 | Manual | Pass
Control Panel Mode-DSE | 0 | 7010102722 | 10 | 4 | 772 | 9 | Manual | Pass
Control Panel Mode-DSE | 0 | 7010102722 | 10 | 4 | 772 | 10 | Manual | Pass
Control Panel Mode-DSE | 0 | 7010102722 | 10 | 4 | 772 | 11 | Manual | Pass
Control Panel Mode-DSE | 0 | 7010102722 | 10 | 4 | 772 | 12 | Manual | Pass
Control Panel Mode-DSE | 0 | 7010102722 | 10 | 4 | 772 | 13 | Manual | Pass
Control Panel Mode-DSE | 0 | 7010102722 | 10 | 4 | 772 | 14 | Manual | Pass
Control Panel Mode-DSE | 0 | 7010102722 | 10 | 4 | 772 | 15 | Manual | Pass
Emergency Stop Alarm | 0 | 7010102722 | 10 | 4 | 39425 | 0 | Ok | Pass
Emergency Stop Alarm | 0 | 7010102722 | 10 | 4 | 39425 | 4096 | Ok | Pass
Emergency Stop Alarm | 0 | 7010102722 | 10 | 4 | 39425 | 8192 | Warning | Pass
Emergency Stop Alarm | 0 | 7010102722 | 10 | 4 | 39425 | 12288 | Shutdown | Pass
Emergency Stop Alarm | 0 | 7010102722 | 10 | 4 | 39425 | 16384 | Shutdown | Pass
Emergency Stop Alarm | 0 | 7010102722 | 10 | 4 | 39425 | 20480 | Ok | Pass
Emergency Stop Alarm | 0 | 7010102722 | 10 | 4 | 39425 | 24576 | Ok | Pass
Emergency Stop Alarm | 0 | 7010102722 | 10 | 4 | 39425 | 28672 | Ok | Pass
Emergency Stop Alarm | 0 | 7010102722 | 10 | 4 | 39425 | 32768 | Ok | Pass
Emergency Stop Alarm | 0 | 7010102722 | 10 | 4 | 39425 | 36864 | Ok | Pass
Emergency Stop Alarm | 0 | 7010102722 | 10 | 4 | 39425 | 40960 | Warning | Pass
Emergency Stop Alarm | 0 | 7010102722 | 10 | 4 | 39425 | 45056 | Ok | Pass
Emergency Stop Alarm | 0 | 7010102722 | 10 | 4 | 39425 | 49152 | Ok | Pass
Emergency Stop Alarm | 0 | 7010102722 | 10 | 4 | 39425 | 53248 | Ok | Pass
Emergency Stop Alarm | 0 | 7010102722 | 10 | 4 | 39425 | 57344 | Ok | Pass
Emergency Stop Alarm | 0 | 7010102722 | 10 | 4 | 39425 | 61440 | Ok | Pass
Under Frequency | 0 | 7010102722 | 10 | 4 | 39426 | 0 | Ok | Pass
Under Frequency | 0 | 7010102722 | 10 | 4 | 39426 | 16 | Ok | Pass
Under Frequency | 0 | 7010102722 | 10 | 4 | 39426 | 32 | Warning | Pass
Under Frequency | 0 | 7010102722 | 10 | 4 | 39426 | 48 | Shutdown | Pass
Under Frequency | 0 | 7010102722 | 10 | 4 | 39426 | 64 | Shutdown | Pass
Under Frequency | 0 | 7010102722 | 10 | 4 | 39426 | 80 | Ok | Pass
Under Frequency | 0 | 7010102722 | 10 | 4 | 39426 | 96 | Ok | Pass
Under Frequency | 0 | 7010102722 | 10 | 4 | 39426 | 112 | Ok | Pass
Under Frequency | 0 | 7010102722 | 10 | 4 | 39426 | 128 | Ok | Pass
Under Frequency | 0 | 7010102722 | 10 | 4 | 39426 | 144 | Ok | Pass
Under Frequency | 0 | 7010102722 | 10 | 4 | 39426 | 160 | Warning | Pass
Under Frequency | 0 | 7010102722 | 10 | 4 | 39426 | 176 | Ok | Pass
Under Frequency | 0 | 7010102722 | 10 | 4 | 39426 | 192 | Ok | Pass
Under Frequency | 0 | 7010102722 | 10 | 4 | 39426 | 208 | Ok | Pass
Under Frequency | 0 | 7010102722 | 10 | 4 | 39426 | 224 | Ok | Pass
Under Frequency | 0 | 7010102722 | 10 | 4 | 39426 | 240 | Ok | Pass
Over Frequency | 0 | 7010102722 | 10 | 4 | 39426 | 0 | Ok | Pass
Over Frequency | 0 | 7010102722 | 10 | 4 | 39426 | 1 | Ok | Pass
Over Frequency | 0 | 7010102722 | 10 | 4 | 39426 | 2 | Warning | Pass
Over Frequency | 0 | 7010102722 | 10 | 4 | 39426 | 3 | Shutdown | Pass
Over Frequency | 0 | 7010102722 | 10 | 4 | 39426 | 4 | Shutdown | Pass
Over Frequency | 0 | 7010102722 | 10 | 4 | 39426 | 5 | Ok | Pass
Over Frequency | 0 | 7010102722 | 10 | 4 | 39426 | 6 | Ok | Pass
Over Frequency | 0 | 7010102722 | 10 | 4 | 39426 | 7 | Ok | Pass
Over Frequency | 0 | 7010102722 | 10 | 4 | 39426 | 8 | Ok | Pass
Over Frequency | 0 | 7010102722 | 10 | 4 | 39426 | 9 | Ok | Pass
Over Frequency | 0 | 7010102722 | 10 | 4 | 39426 | 10 | Warning | Pass
Over Frequency | 0 | 7010102722 | 10 | 4 | 39426 | 11 | Ok | Pass
Over Frequency | 0 | 7010102722 | 10 | 4 | 39426 | 12 | Ok | Pass
Over Frequency | 0 | 7010102722 | 10 | 4 | 39426 | 13 | Ok | Pass
Over Frequency | 0 | 7010102722 | 10 | 4 | 39426 | 14 | Ok | Pass
Over Frequency | 0 | 7010102722 | 10 | 4 | 39426 | 15 | Ok | Pass
Low AC Voltage | 0 | 7010102722 | 10 | 4 | 39427 | 0 | Ok | Pass
Low AC Voltage | 0 | 7010102722 | 10 | 4 | 39427 | 4096 | Ok | Pass
Low AC Voltage | 0 | 7010102722 | 10 | 4 | 39427 | 8192 | Warning | Pass
Low AC Voltage | 0 | 7010102722 | 10 | 4 | 39427 | 12288 | Shutdown | Pass
Low AC Voltage | 0 | 7010102722 | 10 | 4 | 39427 | 16384 | Shutdown | Pass
Low AC Voltage | 0 | 7010102722 | 10 | 4 | 39427 | 20480 | Ok | Pass
Low AC Voltage | 0 | 7010102722 | 10 | 4 | 39427 | 24576 | Ok | Pass
Low AC Voltage | 0 | 7010102722 | 10 | 4 | 39427 | 28672 | Ok | Pass
Low AC Voltage | 0 | 7010102722 | 10 | 4 | 39427 | 32768 | Ok | Pass
Low AC Voltage | 0 | 7010102722 | 10 | 4 | 39427 | 36864 | Ok | Pass
Low AC Voltage | 0 | 7010102722 | 10 | 4 | 39427 | 40960 | Warning | Pass
Low AC Voltage | 0 | 7010102722 | 10 | 4 | 39427 | 45056 | Ok | Pass
Low AC Voltage | 0 | 7010102722 | 10 | 4 | 39427 | 49152 | Ok | Pass
Low AC Voltage | 0 | 7010102722 | 10 | 4 | 39427 | 53248 | Ok | Pass
Low AC Voltage | 0 | 7010102722 | 10 | 4 | 39427 | 57344 | Ok | Pass
Low AC Voltage | 0 | 7010102722 | 10 | 4 | 39427 | 61440 | Ok | Pass
High AC Voltage | 0 | 7010102722 | 10 | 4 | 39427 | 0 | Ok | Pass
High AC Voltage | 0 | 7010102722 | 10 | 4 | 39427 | 256 | Ok | Pass
High AC Voltage | 0 | 7010102722 | 10 | 4 | 39427 | 512 | Warning | Pass
High AC Voltage | 0 | 7010102722 | 10 | 4 | 39427 | 768 | Shutdown | Pass
High AC Voltage | 0 | 7010102722 | 10 | 4 | 39427 | 1024 | Shutdown | Pass
High AC Voltage | 0 | 7010102722 | 10 | 4 | 39427 | 1280 | Ok | Pass
High AC Voltage | 0 | 7010102722 | 10 | 4 | 39427 | 1536 | Ok | Pass
High AC Voltage | 0 | 7010102722 | 10 | 4 | 39427 | 1792 | Ok | Pass
High AC Voltage | 0 | 7010102722 | 10 | 4 | 39427 | 2048 | Ok | Pass
High AC Voltage | 0 | 7010102722 | 10 | 4 | 39427 | 2304 | Ok | Pass
High AC Voltage | 0 | 7010102722 | 10 | 4 | 39427 | 2560 | Warning | Pass
High AC Voltage | 0 | 7010102722 | 10 | 4 | 39427 | 2816 | Ok | Pass
High AC Voltage | 0 | 7010102722 | 10 | 4 | 39427 | 3072 | Ok | Pass
High AC Voltage | 0 | 7010102722 | 10 | 4 | 39427 | 3328 | Ok | Pass
High AC Voltage | 0 | 7010102722 | 10 | 4 | 39427 | 3584 | Ok | Pass
High AC Voltage | 0 | 7010102722 | 10 | 4 | 39427 | 3840 | Ok | Pass
High Current | 0 | 7010102722 | 10 | 4 | 39430 | 0 | Ok | Pass
High Current | 0 | 7010102722 | 10 | 4 | 39430 | 4096 | Ok | Pass
High Current | 0 | 7010102722 | 10 | 4 | 39430 | 8192 | Warning | Pass
High Current | 0 | 7010102722 | 10 | 4 | 39430 | 12288 | Shutdown | Pass
High Current | 0 | 7010102722 | 10 | 4 | 39430 | 16384 | Shutdown | Pass
High Current | 0 | 7010102722 | 10 | 4 | 39430 | 20480 | Ok | Pass
High Current | 0 | 7010102722 | 10 | 4 | 39430 | 24576 | Ok | Pass
High Current | 0 | 7010102722 | 10 | 4 | 39430 | 28672 | Ok | Pass
High Current | 0 | 7010102722 | 10 | 4 | 39430 | 32768 | Ok | Pass
High Current | 0 | 7010102722 | 10 | 4 | 39430 | 36864 | Ok | Pass
High Current | 0 | 7010102722 | 10 | 4 | 39430 | 40960 | Warning | Pass
High Current | 0 | 7010102722 | 10 | 4 | 39430 | 45056 | Ok | Pass
High Current | 0 | 7010102722 | 10 | 4 | 39430 | 49152 | Ok | Pass
High Current | 0 | 7010102722 | 10 | 4 | 39430 | 53248 | Ok | Pass
High Current | 0 | 7010102722 | 10 | 4 | 39430 | 57344 | Ok | Pass
High Current | 0 | 7010102722 | 10 | 4 | 39430 | 61440 | Ok | Pass
kW Overload | 0 | 7010102722 | 10 | 4 | 39432 | 0 | Ok | Pass
kW Overload | 0 | 7010102722 | 10 | 4 | 39432 | 16 | Ok | Pass
kW Overload | 0 | 7010102722 | 10 | 4 | 39432 | 32 | Warning | Pass
kW Overload | 0 | 7010102722 | 10 | 4 | 39432 | 48 | Shutdown | Pass
kW Overload | 0 | 7010102722 | 10 | 4 | 39432 | 64 | Shutdown | Pass
kW Overload | 0 | 7010102722 | 10 | 4 | 39432 | 80 | Ok | Pass
kW Overload | 0 | 7010102722 | 10 | 4 | 39432 | 96 | Ok | Pass
kW Overload | 0 | 7010102722 | 10 | 4 | 39432 | 112 | Ok | Pass
kW Overload | 0 | 7010102722 | 10 | 4 | 39432 | 128 | Ok | Pass
kW Overload | 0 | 7010102722 | 10 | 4 | 39432 | 144 | Ok | Pass
kW Overload | 0 | 7010102722 | 10 | 4 | 39432 | 160 | Warning | Pass
kW Overload | 0 | 7010102722 | 10 | 4 | 39432 | 176 | Ok | Pass
kW Overload | 0 | 7010102722 | 10 | 4 | 39432 | 192 | Ok | Pass
kW Overload | 0 | 7010102722 | 10 | 4 | 39432 | 208 | Ok | Pass
kW Overload | 0 | 7010102722 | 10 | 4 | 39432 | 224 | Ok | Pass
kW Overload | 0 | 7010102722 | 10 | 4 | 39432 | 240 | Ok | Pass
Common Alarm Status | 0 | 7010102722 | 10 | 4 | 774 | 0 | Ok | Check
Common Alarm Status | 0 | 7010102722 | 10 | 4 | 774 | 1 | Warning | Check
Common Alarm Status | 0 | 7010102722 | 10 | 4 | 774 | 2 | Electrical Trip | Check
Common Alarm Status | 0 | 7010102722 | 10 | 4 | 774 | 3 | - | Check
Common Alarm Status | 0 | 7010102722 | 10 | 4 | 774 | 4 | Shutdown | Check
Common Alarm Status | 0 | 7010102722 | 10 | 4 | 774 | 5 | Shutdow/Warn | Check
Common Alarm Status | 0 | 7010102722 | 10 | 4 | 774 | 6 | Shutdow/Elec Trip | Check
Common Alarm Status | 0 | 7010102722 | 10 | 4 | 774 | 7 | Total Failure | Check
Common Alarm Status | 0 | 7010102722 | 10 | 4 | 774 | 8 | - | Check
Common Alarm Status | 0 | 7010102722 | 10 | 4 | 774 | 9 | - | Check
Common Alarm Status | 0 | 7010102722 | 10 | 4 | 774 | 10 | - | Check
Common Alarm Status | 0 | 7010102722 | 10 | 4 | 774 | 11 | - | Check
Common Alarm Status | 0 | 7010102722 | 10 | 4 | 774 | 12 | - | Check
Common Alarm Status | 0 | 7010102722 | 10 | 4 | 774 | 13 | - | Check
Common Alarm Status | 0 | 7010102722 | 10 | 4 | 774 | 14 | - | Check
Common Alarm Status | 0 | 7010102722 | 10 | 4 | 774 | 15 | - | Check
Engine Status | 0 | 7010102722 | 10 | 4 | 48640 | 0 | Off | Check
Engine Status | 0 | 7010102722 | 10 | 4 | 48640 | 1 | On | Check

## j1939_fault
description | resource | device.id | snapshot.source_address | snapshot.dtc | expected_value | snapshot.active | Tc.ref
Medium Fault- SPEED ADJUSTMENT SWITCH : WARNING | 0 | 7020016917 | 234 | 1660944555 | SPEED ADJUSTMENT SWITCH : WARNING | TRUE

## j1939_fault_resync
Description | resource | device.id | snapshot.source_address | snapshot.dtc | expected_value | snapshot.active | Tc.ref
SPEED ADJUSTMENT SWITCH : WARNING | 0 | 7020016917 | 234 | 1676992528 | DTC: Genie, Code: 16, Category: 20, Source: | TRUE | genie_regression.J1939 Faults_Boom Faults